Triangle Spill box Vacuum Testing System

WARNING! Do not exceed 30” WC vacuum on spill boxes at any time.

Purpose:

The system is used to test spill boxes for leaks at a specific level without the need to seal every surface saving hours of unneeded repairs.

The system consists of: a transparent plate with a soft seal, which sits on top of the spill box, a vacuum generating pump to provide the testing vacuum, a vacuum relief valve to keep the vacuum level near 28” WC and protect the box, a gauge port to allow confirmation of the vacuum pulled.

Notes:

- Don’t use the vacuum gauge as a “test criteria” for pass or failure.

- Only add test fluid to the proper testing level. Don’t test areas not required to be tested, as it will only add costs to your customer’s repairs.

- The test plate does not completely seal the top, but provides enough sealing to allow 28” WC vacuum to be applied to the box area.

- If vacuum can’t be achieved, look for leak areas in spill box such as missing gaskets, open drain valves, loose adaptors, etc.

- If bubbles exist, but you can’t see the location of the leak, lower test fluid level down to suspected leak level and repeat test.

Basic Process:

- Add testing fluid to the testing level in the box, pull a vacuum, look for bubbles indicating a leak, and repair leaks and retest as needed.

Testing Procedure:

- Clean debris and liquid from box and top surface of box,

- Add testing fluid to test level,

- Record box and testing information, such as manufacturer, Style, size, depth, diameter, date/time, fluid level, tester’s name, company name,

- Install test plate, attached vacuum gauge to port 1, attached vacuum generator to port 2,

- With valve closed, attach air/nitrogen hose to vacuum generator,

- SLOWLY, open valve to start pulling vacuum,

- Monitor gauge as vacuum builds to 28” WC. Do not exceed 28” WC.

- Look for stream of bubbles on surface of liquid.

- If bubbles exist, test fails, if no bubbles exists, test passes,

- Close valve, remove air/nitrogen hose, remove test plate, remove test fluid, wipe out box,

- Document results such as vacuum pulled for test, test results, Pass or Fail, repairs made, location of any leaks found.

Edited 11/28/11, Copyrighted 3/1998, Michael Lessley